Standard Operating Procedure: HVAC Refrigerant Compliance

1.	Purpose

To establish procedures for compliant operation and maintenance of HVAC systems including refrigerant management in accordance with NYS OCM environmental regulations and federal requirements.

2.	Scope

This SOP applies to all personnel involved in HVAC system operation, maintenance, and refrigerant handling in licensed cannabis cultivation facilities.

3.	Prerequisites

Required prerequisites:
• HVAC systems must be installed by licensed contractors
• Understanding of OCM Section 125.1(c)(1) requirements
• EPA Section 608 certification for refrigerant handling
• Equipment manufacturer specifications available

4.	Responsibilities

Key personnel:
• Facility Manager: Ensures HVAC compliance and maintenance contracts
• Operations Manager: Monitors system performance
• Certified HVAC Technician: Performs refrigerant work (EPA certified)
• Cultivation Manager: Reports environmental control issues

5.	Materials

Required materials:
• Approved refrigerants (low-GWP per OCM regulations)
• Refrigerant tracking logs
• Leak detection equipment
• Temperature and humidity monitors
• Maintenance documentation forms
• PPE for refrigerant handling

6.	Procedure

6.1 Refrigerant Selection Compliance
   a. Per Section 125.1(c)(1), HVAC equipment must use refrigerants that:
      - Have a 100-year global warming potential (GWP) of 750 or less, OR
      - Use naturally occurring refrigerants, OR
      - Meet requirements of Environmental Conservation Law Section 19-0329
   b. Prohibited: High-GWP refrigerants (R-410A GWP >2000)
   c. Approved alternatives: R-32, R-290, R-1234yf, CO2, ammonia
   d. Document refrigerant type in all equipment

6.2 System Installation and Documentation
   a. Ensure installation by licensed HVAC contractor
   b. Verify refrigerant type meets OCM requirements
   c. Record initial refrigerant charge amounts
   d. Obtain and file equipment specifications
   e. Register systems in maintenance tracking

6.3 Leak Detection and Monitoring
   a. Conduct monthly visual inspections of:
      - Refrigerant lines and connections
      - Compressor units
      - Evaporator and condenser coils
   b. Use electronic leak detectors quarterly
   c. Monitor system pressures for anomalies
   d. Check refrigerant levels during maintenance

6.4 Leak Response Procedures
   a. If leak detected:
      - Document location and estimated severity
      - Restrict access to affected area
      - Ventilate space if indoor leak
      - Contact certified HVAC technician immediately
   b. Repairs must be made within 30 days of detection
   c. Document all leak repairs and refrigerant additions
   d. Report significant leaks per EPA requirements

6.5 Refrigerant Handling Requirements
   a. Only EPA Section 608 certified technicians may:
      - Add refrigerant to systems
      - Recover refrigerant from systems
      - Repair refrigerant leaks
   b. Recover refrigerant before servicing sealed systems
   c. Never vent refrigerants to atmosphere
   d. Use proper recovery equipment

6.6 Routine Maintenance Schedule
   a. Monthly:
      - Check system operation and temperatures
      - Inspect for visible leaks or damage
      - Clean or replace air filters
   b. Quarterly:
      - Professional inspection of refrigerant systems
      - Electronic leak detection
      - Coil cleaning
   c. Annually:
      - Comprehensive system audit
      - Refrigerant level verification
      - Performance efficiency testing

6.7 Documentation and Recordkeeping
   a. Maintain refrigerant tracking log including:
      - Equipment identification
      - Refrigerant type and GWP
      - Amounts added or recovered
      - Leak repairs and dates
   b. Retain service records for minimum 3 years
   c. Make records available for OCM inspection
   d. Include in Energy and Environmental Plan

6.8 Equipment Replacement Planning
   a. Inventory all equipment with non-compliant refrigerants
   b. Develop replacement schedule before equipment failure
   c. Prioritize high-GWP systems for replacement
   d. Select replacement equipment meeting current standards

7.	References

• NYS OCM Regulations Section 125.1(c)(1) - HVAC Standards
• Energy and Environmental Plan Guidance (OCM)
• EPA Section 608 Refrigerant Regulations
• Environmental Conservation Law Section 19-0329

8.	Definitions

• GWP: Global Warming Potential (100-year measure)
• HVAC: Heating, Ventilation, and Air Conditioning
• Low-GWP: Refrigerants with GWP ≤750
• EPA Section 608: Federal refrigerant handling certification

9.	Sources

Information obtained from:
• NYS Office of Cannabis Management: https://cannabis.ny.gov/
• Energy and Environmental Plan Guidance (OCM, November 2024)
• EPA Refrigerant Regulations

Related SOPs and Cross-References

Category: ENVIRONMENT - NYS OCM

The following SOPs are related to this procedure:

GEN-052: Energy Environmental Plan Development - Part of EEP compliance

GEN-055: Greenhouse Gas Emissions Management - Refrigerant emissions

GEN-039: Energy Resource Tracking - HVAC energy tracking

CULT-009: Dehumidification Operation - Climate control

CULT-015: Air Quality Ventilation - HVAC integration

GEN-012: Preventive Maintenance - Equipment maintenance

Note: This SOP is part of a comprehensive cannabis compliance system. SOPs marked "(OTHER STATES)" contain recommendations from other state programs and are suggestions, not NYS OCM requirements.